Modbus DDF Request Form

Thank you for your interest in Schneider Electric APC multi-vendor support for StruxureWare Central / StruxureWare Data Center Expert. Please provide the following:

- Customer and device information

- Vendor documentation regarding the Modbus register map

Customer information

| Company name | NAV Canada |
| --- | --- |
| Contact name | Yang Gao |
| E-mail address | gaoya@navcanada.ca |
| Phone number | 613-563-7420 |
| Address | 77 Metcalfe Street |
| Date | 2018-02-05 |

Device information

| Vendor name | Deep Sea Electronics |
| --- | --- |
| Device model name/number | DSE 7420 |
| Device type Select one from list | Generator Controller |  |
| Do you use StruxureWare Operations? If yes, specify version | No |
| Is the device behind a gateway? If yes, is it the TSXETG100? | No |

Define the values to be included in the DDF

| Data Point | Modbus Register | Units | Scaling |
| --- | --- | --- | --- |
| Control Mode | 772 (page 3, offset 4) |  | 1 |
| Warning Alarm Active | 774 (page 3, offset 6, bit 11) |  |  |
| Electrical Trip Alarm Active | 774 (page 3, offset 6, bit 12) |  |  |
| Shutdown Alarm Active | 774 (page 3, offset 6, bit 13) |  |  |
| Control Unit Failure | 774 (page 3, offset 6, bit 14) |  |  |
| Control Unit Not Configured | 774 (page 3, offset 6, bit 16) |  |  |
| Mains Voltage L1-N | 1060 (page 4, offset 36-37) | V | 0.1 |
| Mains Voltage L2-N | 1062 (page 4, offset 38-39) | V | 0.1 |
| Mains Voltage L3-N | 1064 (page 4, offset 40-41) | V | 0.1 |
| Mains Voltage L1-L2 | 1066 (page 4, offset 42-43) | V | 0.1 |
| Mains Voltage L2-L3 | 1068 (page 4, offset 44-45) | V | 0.1 |
| Mains Voltage L3-L1 | 1070 (page 4, offset 46-47) | V | 0.1 |
| Mains Current L1 | 1076 (page 4, offset 52-53) | A | 0.1 |
| Mains Current L2 | 1078 (page 4, offset 54-55) | A | 0.1 |
| Mains Current L3 | 1080 (page 4, offset 56-57) | A | 0.1 |
| Room Temperature | 1335 (page 5, offset 55) | Degree C |  |
| Mains Total Watts | 1560 (page 6, offset 24-25) | W | 1 |
| Mains Total VA | 1568 (page 6, offset 32-33) | VA | 1 |
| Mains Total VAr | 1576 (page 6, offset 40-41) | VAr | 1 |
| Mains Average Power Factor | 1581 (page 6, offset 45) |  | 0.01 |
| Low Fuel | 43524 (page 170, offset 4) |  |  |
| Fuel Leak | 43526 (page 170, offset 6) |  |  |

Incorrect or unfiltered data points and Modbus Registers may result in a request rejection.

Additional information

Please enter any additional information about this request:

Remove the sensors that are crossed out below:

Remove the alarms ranging from register 2049 to 2055. Those registers are not valid for DSE 7420 controller.

Note that specific sensor requests are not guaranteed.

The Schneider Electric APC approach is to support all of the devices that comprise your critical power and cooling infrastructure, regardless of manufacturer. With the Enterprise suite of products, end-users and solution providers can select the appropriate SNMP or Modbus enabled equipment without worrying whether or not it will be supported by their monitoring solution. Schneider Electric has designed StruxureWare Central / StruxureWare Data Center Expert with open architecture to provide support for their power and cooling SNMP or Modbus enabled device, which will allow customers one management system to monitor their physical infrastructure.

This approach is unique in the industry.

To request multi vendor support please e-mail the information requested to StruxureWare Data Center Expert team at multivendorsupport@apc.com.

Please note that requesting a third party SNMP or Modbus DDF does not guarantee that APC will create the DDF.

Additionally, the turn around time for a DDF file can fluctuate based on the number of requests already in-process, and tend to be longer during critical times in the StruxureWare Data Center Expert release cycle.